INDIAN INSTITUTE OF TECHNOLOGY MADRAS

ENGINEERING UNIT – ELECTRICAL DIVISION

Date : 09/12/2013

CORRIGENDUM & MINUTES OF PRE-BID MEETING HELD ON 6/12/13

Tender No. 34/2013-14/ELDB

Name of the work : Provision and installing 500kVA DG set for Electrical Sciences Block in IIT Madras

| Sl No. | Queries from contractors | Clarifications given by IIT Madras |
| --- | --- | --- |
| 1 | BOQ in Price Bid Item No. 2 | Read as “ AMF Panel “ instead of built-in AMF Panel (inside the acoustic enclosure). No change in other specifications but Bypass switch is to be introduced. |
| 2 | EMD | No change in the mode of submission of EMD. EMD in the form of DD only is acceptable. |
| 3 | Foundation for DG | Construction of foundation as recommended by the manufacturer of the Gen. Set is included in the scope of Item No. 1 in BOQ. |
| 4 | DG Set specifications, Inspection and testing. Payment terms and Guarantee | The specification and testing procedure shall be followed as per CPWD General Specifications for Electrical Works – Part VII (DG Set). |
| 5 | C Form | IIT Madras will not issue any “ C “ form |
| 6 | Aluminium cladding work for silencer | The item of exhaust pipe includes the insulation and Aluminium cladding of the pipe and the silencer. |
| 7 | Request to consider issuing two separate orders for equipment and other related works. | Due to some administrative reason, this request can not be considered. |

Sd-

Executive Engineer (E)