TECHNICAL SPECIFICATIONS

1kVA UPS True On Line, Sine wave Output without isolation transformer

Technology  :

PWM technology in True on-line operation, employing double conversion method using

MOSFETs / IGBTs.

Method of Inversion  :

Adaptive pulse width modulation or weighted pulse width modulation with high

Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.     Input Voltage Range @ F.L				              :  180V-270V AC

2.     Input Power Factor @ F.L					:  > 0.95

3.     Input Frequency Variation					: 50 Hz ± 5%

4.     Total Energy storage capacity of Battery ( in one               :

String)  @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 36V Bus | 48V Bus |
| 15 min | >250 Watt Hr | >250 Watt Hr |

5.    AC Output Voltage and steady state Regulation @ F.L       	: 230V AC; better than  ± 1%

6.     Transient Voltage Regulation at Step Load 			: < 5%

7.     Maximum deliverable continuous Output Power 			: >800W

8.     Output Frequency 						: 50 Hz ± 4%(Synchronous  to mains)

50 Hz ( 0.5%(Free running ).

9.     Efficiency

(i)  Battery mode						: > 80%

(ii) Mains mode		   				: > 80%

10.     THD @ F.L  						              : <3% (for linear load); <5%(for nonlinear load)

11.   Crest Factor @ F.L						: > 3 : 1

12. Over Load Duration @ 110%, 125% and 150% of F.L	: 5 min, 1 min and  2 sec respectively

13.   Static bypass switch : Bi-directional with change over time less than 10 milliseconds in free running mode and

instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.  Temperature and Humidity

(i)    Operating Temperature Range				: upto 40ºC

(ii)   Humidity						: upto 95% Rh

15.   Noise level (at 1 meter)				  	: < 45 dB

16.   Conformance to Standards

(i)   EMC Standards					  	: IEC 801-2,3,4,5

(ii)  Emission Standard					: EN55022 Class B

(iii) Safety Standard					  	: EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a) Current limiting ,Over load and Short circuit protection.

b) Phase locking mechanism with mains frequency.

c) Over voltage / Under voltage protection.

d) All other protection systems as required for safety  of the system.

Warranty and AMC

1.  3 years Warranty Period for UPS  as well as  Batteries.

2. Comprehensive AMC covering the batteries, after the expiry of warranty period

Important instructions:

a)  Quote should indicate the Model/Series Name and Model Number of UPS

# Annexure-D1

# TECHNICAL SPECIFICATIONS

1kVA UPS True On Line, Sine wave Output

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching (>10 kHz for MOSFETs and >5 kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	180V-270V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 36V Bus | 48V Bus |
| For 30 min | > 864 Watt Hr | > 864 Watt Hr |
| For 60 min | > 1440 Watt Hr | > 1440 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 800W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 80%

(ii)	Mains mode	: 	> 80%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

2kVA UPS True On Line, Sine wave Output

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	170V-270V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 48 V Bus | 72 / 96 V Bus |
| For 30 min | > 2016 Watt Hr | > 2304 Watt Hr |
| For 60 min | > 3120 Watt Hr | > 3648 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 1600W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 80%

(ii)	Mains mode	: 	> 80%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	With external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

3kVA UPS True On Line, Sine wave Output

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	170V-270V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 96 V Bus | 192 V Bus |
| For 30 min | > 2880 Watt Hr | > 2880 Watt Hr |
| For 60 min | > 6240 Watt Hr | > 4608 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 2400W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 83%

(ii)	Mains mode	: 	> 85%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

5kVA UPS True On Line, Sine wave Output

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	180V-270 V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 192 V Bus |
| For 30 min | > 4608 Watt Hr |
| For 60 min | > 7680 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	>4000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 87%

(ii)	Mains mode	: 	> 85%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

10kVA UPS True On Line, Sine wave Output (3 ø i/p & 1 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	374V-506 V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 9600 Watt Hr |
| For 60 min | > 15600 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 8000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

10kVA UPS True On Line, Sine wave Output (1 ø i/p & 1 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	180V-270 V AC

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 9600 Watt Hr |
| For 60 min | > 15600 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 8000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

15kVA UPS True On Line, Sine wave Output (3 ø i/p & 1 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.93

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 15600 Watt Hr |
| For 60 min | > 24000 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 12000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

15kVA UPS True On Line, Sine wave Output (3 ø i/p & 3 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.93

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 15600 Watt Hr |
| For 60 min | > 24000 Watt Hr |

5 a.	AC Output Voltage and steady state Regulation @ FL	: 	415V AC; < 1% (for balanced load)

< 2% (for 100% unbalanced load)

5 b.	Phase displacement	:	< 1º (for balanced load)

< 2º (for 100% unbalanced load)

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 12000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

20kVA UPS True On Line, Sine wave Output (3 ø i/p & 1 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 15600 Watt Hr |
| For 60 min | > 24000 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	>16000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

20kVA UPS True On Line, Sine wave Output (3 ø i/p & 3 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.95

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 240 V Bus |
| For 30 min | > 15600 Watt Hr |
| For 60 min | > 24000 Watt Hr |

5 a.	AC Output Voltage and steady state Regulation @ FL	: 	415V AC; < 1% (for balanced load)

< 2% (for 100% unbalanced load)

5 b.	Phase displacement	:	< 1º (for balanced load)

< 2º (for 100% unbalanced load)

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 16000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   	Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

30kVA UPS True On Line, Sine wave Output (3 ø i/p & 1 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.93

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 360 V Bus |
| For 30 min | > 28800 Watt Hr |
| For 60 min | > 46800 Watt Hr |

5.	AC Output Voltage and steady state Regulation @ FL	: 	230V AC; better than ± 1%

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 24000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS

# TECHNICAL SPECIFICATIONS

30kVA UPS True On Line, Sine wave Output (3 ø i/p & 3 ø o/p)

Technology:

PWM technology in True on-line operation, employing double conversion method using MOSFETs / IGBTs.

Method of Inversion:

Adaptive pulse width modulation or weighted pulse width modulation with high Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.	Input Voltage Range @ F.L	:	415V ± 15%

2.	Input Power Factor @ F.L	:  	> 0.93

3.	Input Frequency Variation	: 	50 Hz ± 5%

4.	Total Energy storage capacity of Battery (in one string) @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 360 V Bus |
| For 30 min | > 28800 Watt Hr |
| For 60 min | > 46800 Watt Hr |

5 a.	AC Output Voltage and steady state Regulation @ FL	: 	415V AC; < 1% (for balanced load)

< 2% (for 100% unbalanced load)

5 b.	Phase displacement	:	< 1º (for balanced load)

< 2º (for 100% unbalanced load)

6.	Transient Voltage Regulation at Step Load 	: 	< 5%

7.	Maximum deliverable continuous Output Power 	: 	> 24000W

8.	Output Frequency 	: 	50 Hz (  4% (Synchronous to mains)

50 Hz (  0.5% (Free running)

9.	Efficiency

(i)	Battery mode	: 	> 84%

(ii)	Mains mode	: 	> 89%

10.     THD @ F.L  	: 	< 3% (for linear load);

< 5% (for nonlinear load)

11.   Crest Factor @ F.L	: 	> 3 : 1

12. 	Over Load Duration @ 110%, 125% and 150% of F.L	: 	5 min, 1 min and 2 sec respectively

13.	Static bypass switch: Bi-directional with change over time less than 10 milliseconds in free running 	mode and instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.	Temperature and Humidity

(i)    Operating Temperature Range	: 	upto 40ºC

(ii)   Humidity	: 	upto 95% Rh

15.	Noise level (at 1 meter)	:  	< 45 dB

16.	Conformance to Standards

(i)   EMC Standards	: 	IEC 801 - 2,3,4,5

(ii)  Emission Standard	: 	EN55022 Class B

(iii) Safety Standard	: 	EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a)	Isolation - Output shall be fully isolated from mains and with surge /spike suppressors 	incorporated.

b) 	Current limiting, over load and Short circuit protection.

c) 	Phase locking mechanism with mains frequency.

d) 	Over voltage / Under voltage protection.

e) 	All other protection systems as required for safety of the system.

Other Features:

1.	Cold start feature under full load condition.

2.	Standard hardware / software support for serial communication interface and SNMP / Web 	monitoring.

3.	Auto shut down and energy saving features.

4.   	Temperature compensated battery charging for battery life enhancement.

3.   	Automated battery testing and advanced battery management features.

4.    	Sufficient ventilation and forced air cooling through fans.

5.   	Documentation/Manuals support for component level Servicing.

6.   	Serviceability at component level.

7.   	Spares and accessories deliverable along with UPS for Servicing.

## Warranty and AMC:

1.	3 years Warranty Period for UPS as well as Batteries.

2.	Comprehensive AMC covering the batteries, after the expiry of warranty period for the 	configurations

(i) to (iv) given below.

Important instructions:

a) 	Separate quote is invited for each one of the following configurations:

(i)	with built- in isolation transformer and 30 minutes back up time.

(ii)	with built- in isolation transformer and one hour back up time.

(iii)	with external isolation transformer and 30 minutes back up  time.

(iv)	with external isolation  transformer and  one hour back up  time.

b) 	Batteries must be SMF type of following make:

Hitachi, Panasonic, Global Yuasa, Yuasa, Base or Rocket.

c)  	Quote should indicate the Model/Series Name and Model Number of UPS