INDIAN INSTITUTE OF TECHNOLOGY,

MADRAS

- TECHNICAL SPECIFICATION FOR EXHAUST SYSTEM

- EXHAUST SYSTEM SPECIFICATIONS

- MEDIUM PRESSURE CENTRIFUGAL BLOWERS:

The exhaust fans supplied and installed shall be of ‘Centrifugal Corrosion Resistant’ type and shall be capable of delivering the design flow rate against designed pressure drop.

The fans shall be robust in construction and suitable for continuous duty operation. It shall be mounted with ease of maintenance and shall be installed with proper vibration isolators to minimize vibration transmission to ductwork and support structure.

Fans selected shall be silent and vibration free when running and suitable for outdoor use and shall not exceed designed impeller speed.

Aerodynamic performance of the fan shall be tested and comply ‘ISO 5801’ standards.

Sound level shall be tested and comply with ‘ISO 5136.2’ standards.

The casing shall be of self-supporting design, thermoformed (size 400 and below), welded by machine (automatically welded for size 400 and below). The material of construction shall be fire retardant polypropylene (PPs) for fire safety and suitable for use against corrosive ‘medium’ and a maximum allowable operating temperature of 70°C. No metal parts shall be exposed and in contact with the airstream.

Impeller material of construction shall be fire retardant polypropylene (PPs) for fan size up to 400 (polypropylene {PP} for fan size 450 and above) suitable for use against corrosive ‘medium’ and a maximum allowable operating temperature of 70°C. It shall consist of 20 forward curved blades injection molded up to size 710 (thermoformed blades, automatically welded from 800). The impeller balancing shall be tested in accordance to VDI 2060, Q6.3 standards.

Each impeller above size 450 shall be tested in an over speed test stand above its nominal rate and dynamically balanced on two levels in accordance to VDI 2060, Q6.3 standards.

Electro-galvanized stand shall be used to support the fan and the motor for fan sizes up to 400 in view of the corrosive environment. Sturdy metal galvanized steel stand shall be used from fan size 450 onwards.

A standard hub seal shall be fitted onto the impeller hub to prevent the corrosive ‘medium’ from contacting the shaft.

SPECIFICATIONS FOR MOTOR AND ACCESSORIES

Use an electric motors built to IEC standards foot mounted (B5) or Flange mounted (B3), also in ex-protected or multistage versions, for the drive. The impeller hub is coated with aluminum. Power transmission from motor to impeller by means of an impeller directly fixing on the motor shaft in direct driven application. The impeller is fixed on to a flange bearing and the tightening adopter system guarantees secure mechanical connection.

Motor Standard IEC three-phase motors in accordance with IEC.

The fan shall be driven by a standard TEFC electric motor with class ‘F’ insulation and class ‘B’ temperature rise unless otherwise mentioned. Motor shall be suitable for outdoor installation with IP55 protection and suitable for operation with 415V/3Ph/50Hz electrical supply. Motor supplied shall be in accordance to IEC standards.

FUME SCRUBBER SPECIFICATION

### Vertical Flow Fume Scrubbers

- These fume scrubbers are of Single stage packed bed type.  Single Stage packed Bed removes the bulk of the contaminant from the air stream and may be continuously wetted to prevent plugging.

- In a scrubber, water is the media which removes pollutants from the air. When the water is re-circulated, addition of fresh water is necessary to purge contaminants and replace evaporation losses.  Fresh water may be added to the recycle reservoir continuously or periodically.

- Scrubbers are frequently used in applications where the air stream is being treated to remove acid fumes. The addition of chemical may be controlled manually or by a pH controller (Optional)

- Fume scrubbers can be fabricated from PP-FRP with suitable thickness based on the size & volume.The maximum temperature rating for the scrubber is 70° PVC.

- Bolted access ports are provided for inspection of the interior packing and mist eliminator elements. Hardware is MS.

Single Stage Packed Bed scrubbers complete with auxiliaries and options described herein.  The system shall include but is not limited to the following:

- All scrubber internals necessary to provide adequate process capture and 
to achieve the designed performance.

- Mist eliminator to separate the water mist from carrying over.

- Flanged connections for all external water fill, water makeup and drain,overflow piping as required.

- Complete shop coating of required areas with coat or resistant paint for external surfaces.

- Self-contained recirculation pump system.

DESIGN REQUIREMENTS

  - The Scrubber's shall be manufactured using Polypropylene (PP) with FRP lining is used.

  - The Scrubber shall be provided with access ports / doors to allow limited access to the internals of the unit.  The Scrubber shell has flanged pipe connections or female NPT connections for introducing makeup and drain water as well as recirculation liquid connections.

  - The Scrubbers are equipped with random-dumped PP rings packed with appropriate depth of the packing..

  - The Scrubber is equipped with a high efficiency 90%. Material for the mist eliminator is PVC.

  - The fan and motor is designed for system static pressure per application depending on packing depth and mist eliminator selection.  Pressure drop calculations through the Scrubber plus external delta P for the customer’s ductwork losses.

  - Sound levels generated by the Vendor-furnished equipment during normal operation shall not exceed 85 dBA-weighted, slow responses, under free field condition, at a horizontal distance of 10 feet from the surface of sound generation.  The Vendor as optioned will furnish silencers.

STANDARD SUPPLIED COMPONENTS

Standard purchased components furnished on Wet Scrubbers are as follows:

- Complete Scrubber tower including all mist eliminator, water spray nozzles, packing material, scrubber water tank and ladder.

- Piping for recirculation water, make up fresh water & drain connection.

- All manual valve wherever requires within scrubber.

- Scrubber pump.

COMPONENTS SUPPLIED BY END USER

- Civil Foundation for scrubber

- Fresh water for Scrubber

- Required Drain connection to the Scrubber

Water with chemicals is sprayed with high pressure through nozzles into the air flow. Some of the water evaporates, especially if the process-air is hot, and disappear with the exhaust. Water droplets are separated from the exhaust and re-circulated back to the water reservoir. Evaporated water is replaced by fresh water and chemicals. Dust and pollution products from the process are removed periodically through the drain.

SPECIFICATIONS FOR PP/FRP DUCTING AND ACCESSORIES

Technical Specification for PP/FRP Ducting:

- PP means PPGL: One side smooth & glassy finish and other end is mat finish.

    - The smooth surface should be the inner surface of the duct.

    - On mat side, FRP lining to be done.

- FRP Lining to be done on the outer surface of PPGL I.e. on mat side.

  - One layer FRP is approximate one mm.

  - The final layer should be with fine mat to have smooth and good finish.

  - While making the lining, there should not be any air pockets or any sort of Uneven finish.

  - There should be time gap between the FRP layers, allowing each layer to be got dried.

- The flange thickness should be 1.5 times of the duct thickness up to 750 mm and 2 times above 750 mm ducting.

- All flanges are to be matched with M8, GI fasteners and flat washers on both the sides.

- All the flanges should have fasteners at the 4 corners.

- All the fasteners to be fixed at a pitch distance of between 125 mm to 150mm.

- All the flanges should be properly ground and dressed.

- Duct support distance should not be more than 2500 mm.

- Any duct length should not be more than 3600 mm.

- All square / rectangular ducts with more than 1800 mm length should have a brazing frame at the center on the external surface.

- Provide 40 x 40 flanges up 750 mm duct size and 50 x 50 above 750 mm.

- The finish paint should be admiral grey unless specified.

- 5 mm Thick rubber gasket is used between the flanges.