INDIAN INSTITUTE OF TECHNOLOGY,

MADRAS

- TECHNICAL SPECIFICATION FOR LABORATORY

- FURNITURE & FUMEHOOD

- INDEX

| SL. | CHAPTER NAME | DESCRIPTION |
| --- | --- | --- |
| 1 | CHAPTER-01 | LABORATORY FURNITURE SPECIFICATION |
| 2 | CHAPTER-02 | FUMEHOOD SPECIFICATION |

- CHAPTER-01

- LAB FURNITURE SPECIFICATIONS

DESCRIPTION OF WORK

- SUMMARY AND SCOPE

- Section Includes:

  - Furnish all cabinets and casework, including tops, ledges, supporting structures. Include delivery to the building, set in place, level, and scribe to walls and floors as required. Furnish and install all filler panels, knee space panels and scribes as shown on drawings.

  - Furnish and deliver all utility service outlet accessory fittings, electrical receptacles and switches identified on drawings as mounted on the laboratory furniture. All plumbing and electrical fittings, not preinstalled in equipment, will be packaged separately and properly marked for delivery to the appropriate contractor.

  - Furnish and deliver, for installation by the mechanical contractor, all laboratory sinks, cup sinks or drains, drain troughs, overflows and sink outlets with integral tailpieces, which occur above the floor, and where these items are part of the equipment. All tailpieces shall be furnished less the couplings required to connect them to the drain piping system.

  - Furnish service strip supports where specified, and setting in place service tunnels, service turrets, supporting structures and reagent racks of the type shown on the drawings.

  - Removal of all debris, dirt and rubbish accumulated as a result of the installation of the laboratory furniture to an onsite container provided by others, leaving the premises broom clean and orderly.

- BASIS OF WORK

- Laboratory Furniture as the standard of construction for steel laboratory furniture. The construction standards of this product line shall provide the basis for quality and functional installation.

- CABINET STYLE:

- Steel: 
Cabinet bodies, drawer bodies, shelves, drawer heads and door assemblies shall be fabricated from Cold Rolled Steel.

- DRAWER AND DOOR STYLE:

- The outer drawer and door head shall have a channel formation on all four sides to eliminate sharp raw edges of steel and the top front corners shall be welded and ground smooth. Drawer and door, when closed, shall be recessed to create an overall flush face, and with optional pull.

- MATERIALS

- General Requirements:
It is the intent of this specification to provide a high quality steel cabinet specifically designed for the laboratory environment.

- Steel:

- Cold Rolled Steel:
Cold rolled sheet steel shall be prime grade 12, 14, 16, 18 and 20 gauge U.S. Standard; roller leveled, and shall be treated at the mill to be free of scale, ragged edges, deep scratches or other injurious effects.

- Glass: 
Glass used for framed sliding and swinging doors shall be 1/8" float glass. Glass used for unframed sliding doors, shall be 1/4" float glass. Glass used in fume hoods or other hazardous locations shall be 7/32" laminated safety float glass, except the glass shielding fluorescent lights in fume hoods shall be tempered glass to provide greater resistance to heat and impact.

- Drawer and Door Pulls:

- Pull shall be of modern design, offering a comfortable handgrip, and be securely fastened to doors and drawers with screws. All pulls shall be satin finish aluminum, with a clear, lacquer finish. Two pulls shall be required on all drawers over 24" long. Use of plastic pulls (molded or extruded), or a design not compatible for usage by the handicapped will not be acceptable.

- Hinges: 
Hinges shall be made of Type 304 stainless steel .089 thick, 2-1/2” high, with brushed satin finish, and shall be the institutional type with a five-knuckle bullet-type barrel. Hinges shall be attached to both door and case with two screws through each leaf. Welding of hinges to door or case will not be accepted. Doors less than 36" in height shall be hung on one pair of hinges, and doors over 36" high shall be hung on 3 hinges.

- Positive Catch: 
A two-piece heavy-duty cam action positive catch shall be provided on all base cupboard doors and shall be positioned near the pivoting edge of door to provide a clean unobstructed opening. Main body of the catch shall be confined within an integral cabinet divider rail, while latching post shall be mounted on the hinge side of door. Nylon roller type catches are not acceptable.

- Elbow Catches: 
Elbow catches and strike plates shall be used on left hand doors of double door cases where locks are used, and are to be burnished cast aluminum, with bright brass finish.

- Shelf Adjustment Clips: 
Shelf adjustment clips shall be nickel-plated steel.

- Base Molding: 
Base Molding shall be provided on all table legs, unless otherwise specified, to conceal leveling device.  Shoes shall be a pliable, black vinyl material.  Corner clip should be provided to hold the base molding firmly. Use of a leg shoe, which does not conceal leveling device, will not be acceptable

- Sink Supports: 
Sink supports shall be the hanger type, suspended from top front and top rear horizontal rails of sink cabinet by four 1/4" dia. rods, threaded at bottom end and offset at top to hang from two full length reinforcements welded to the front and rear top rails. Two 3/4" x 1-2/2" x 12 gauge channels shall be hung on the threaded rods to provide an adjustable sink cradle for supporting sinks. When sink capacity exceeds 3,750 cu. in., the sink supports shall be suspended from full-length reinforcements welded to the two end rails. Two 1" x 2" x 10 gauge full-length channels shall be hung from the four 1/4" dia. rods to provide an alternate sink cradle.

- CONSTRUCTION

- Steel Base Cabinet Construction:

  - General:

    - The steel furniture shall be of modern design and shall be constructed in accordance with the best practices of the Scientific Laboratory Equipment Industry. First class quality casework shall be insured by the use of proper machinery, tools, dies, fixtures and skilled workmanship to meet the intended quality and quantity for the project.

    - All cabinet bodies shall be flush front construction with intersection of vertical and horizontal case members, such as end panels, top rails, bottoms and vertical posts in same plane without overlap. Exterior corners shall be spot welded with heavy back up reinforcement at exterior corners. All face joints shall be welded and ground smooth to provide a continuous flat plane.

    - Each cabinet shall be complete so that units can be relocated at any subsequent time without requiring field application of finished ends or other such parts.

    - Case openings shall be rabbetted on all four sides for both hinged and sliding doors to provide a dust resistant case.

    - All cabinets shall have a cleanable smooth interior. Bottom edges shall be formed down on sides and back to create easily cleanable corners with no burrs or sharp edges, and front edge shall be offset to create a seamless drawer and door recess rabbet for dust stop.

  - Steel Gauges:
Gauges of steel used in construction of cases shall be 18 gauge, except as follows:

    - Corner gussets for leveling bolts and apron corner braces, 12 gauge.

    - Case and drawer suspension channels, 14 gauge.

    - Top and intermediate front horizontal rails, table aprons, hinge reinforcements, and reinforcement gussets, 16 gauge.

    - Drawer assemblies, door assemblies, bottom, bottom back rail, toe space rail, and adjustable shelves, 20 gauge.

  - Base Cabinets:

    - End uprights shall be formed into not less than a channel formation at top, bottom, back and front. The front edge shall further offset to form a strike for doors and drawers, and shall be perforated for the support of drawer channels, intermediate rails and hinge screws. Upright filler shall be screwed in place in all cupboard units to close the back of the channel at front of the upright and to provide a smooth interior for the cupboard to facilitate cleaning. The upright filler shall be perforated with shelf adjustment holes at not more than 2" centers painted prior to assembly. The inside front of the upright shall be further reinforced with a full height 16 gauge hinge reinforcement angle.

    - Top horizontal rail on base cabinets shall interlock within the flange at top of end panels for strength, but shall be flush as face of unit. Top rail shall have a full width rabbet for swinging doors and drawers. Reinforcements shall be provided at all front corners for additional welded strength between vertical and horizontal case members.

    - Intermediate rails shall be provided between doors and drawers, but shall not be provided between drawers unless made necessary by locks in drawers. When required, intermediate rails shall be recessed behind doors and drawer fronts, and designed so that security panels may be added as required.

    - Intermediate vertical uprights shall be furnished to enclose cupboards when used in a unit in combination with a half width bank of drawers. However, to allow storage of large or bulky objects, no upright of any type shall be used at the center of double door cupboard units.

    - Cabinet bottom, and bottom rail shall be formed of one piece of steel except in corner units and shall be formed down on sides and back to create a square edge transition welded to cabinet end panels, and front edge shall be offset to create a seamless drawer and door recess rabbet for dust stop.

    - Toe space rail shall extend up and forward to engage bottom rail to form a smooth surfaced fully enclosed toe space, 3" deep x 5" high. Whenever toe space base is omitted for units to set on building bases on separate steel bases, then the toe space rail shall extend back 4-1/2".

    - Back construction shall consist of a top and bottom rail, channel formed for maximum strength and welded to back and top flange of end uprights, open for access to plumbing lines.

- Cupboard units only shall be provided with removable back panels.

    - Die formed gussets, with multiple ends for strength, shall be furnished in each bottom corner of base units to insure rigidity, and a 3/8"-16 leveling bolt, 3" long, and shall engage a clinch nut in each gusset. Access to the leveling bolts shall be through plug buttons in the bottom pan. Each leveling bolt and gusset shall be capable of supporting 500 lbs. Access to leveling bolts through toe space or leveling bolts requiring special tools to adjust are not acceptable.

    - Adjustable shelves shall be formed down 3/4", returned back 7/8" and up 1/4" into a channel formation front and rear; formed down 3/4" at each end, shelves over 42" long shall be further reinforced with a channel formation welded to underside of shelf.

    - Drawer bodies shall be made in one-piece construction including the bottom, two sides, back and front. They shall be fully coved at interior bottom on all four sides for easy cleaning. The top front of the inner drawer body shall be offset to interlock with the channel formation in drawer head providing a 3/4" thick drawer head.

    - Drawer suspension assembly shall consist of 2 sections providing a quiet, smooth operation on ball bearing nylon rollers. All drawers shall be self-closing from a point 5" open. Cabinet channels shall maintain alignment of drawer and provide an integral drawer stop, but the drawer shall be removable without the use of tools. Drawers shall provide 13-5/8" front to back clearance when fully extended. Drawers shall rise when opened thus avoiding friction with lower drawers and/or doors. Drawer suspension system shall incorporate a double stop, lock open feature. Case suspension channels shall be Galvanized Steel, drawer suspension channels shall be Cold Rolled Steel. Drawer suspension channels on Stainless Steel Cabinets shall be zinc plated after they are formed.

    - Steel Door assembly (two-piece) for solid pan swinging doors shall consist of an inner and outer door pan. Outer door pan shall be formed at all four sides. The corners on the pull side of the outer door pan shall be welded and ground smooth to prevent exposure of sharp edges of steel at these critical points. Inner door pan shall be flanged at all four sides with hinge reinforcements welded in place. The door assembly shall be 3/4" thick and contains sound deadening material.

    - Steel Drawer/door assemblies shall be painted prior to assembly. Both shall be punched for attaching drawer pulls. Likewise, inner pan formation of door and drawer body shall be indented for in-field installation of locks when required.

    - Doors shall be readily removable and hinges easily replaceable. Hinges shall be applied to the cabinet and door with screws. Welding of hinges to either cabinet or door will not be acceptable.

    - Knee space panels, where shown or specified, shall be 20 gauge, finished same as casework cabinets, and easily removable for access to mechanical service areas.

- PERFORMANCE REQUIREMENTS

- Steel Casework Construction Performance:

  - Base cabinets shall be constructed to support at least a uniformly distributed load 200 lbs. per square foot of cabinet top area, including working surface without objectionable distortion of interference with door and drawer operation.

  - Base cabinet corner gussets with leveling bolts shall support 500 lbs. per corner, at 1-1/2" projection of the leveling bolt below the gusset.

  - Each adjustable and fixed shelf 4 ft. or shorter in length shall support an evenly distributed load of 40 lbs. per square ft. up to a maximum of 200 lbs., with nominal temporary deflection, but without permanent set.

  - Drawer construction and performance shall allow 13-5/8" clear when in an extended position and suspension system shall prevent friction contact with any other drawer or door during opening or closing. All drawers shall operate smoothly, a minimum of 10,000 cycles with an evenly distributed load of 150 lbs.

  - Swinging doors on floor-mounted casework shall support 200 lbs. suspended at a point 12" from hinged side, with door swung through an arc of 160 degrees. Weight load test shall allow only a temporary deflection, without permanent distortion or twist. Door shall operate freely after test and assume a flat plane in a closed position.

- Steel Paint System Finish and Performance Specification:

- Steel Paint System Finish:
After Cold Rolled Steel and Textured Steel component parts have been completely welded together and before finishing, they shall be given a pre-paint treatment to provide excellent adhesion of the finish system to the steel and to aid in the prevention of corrosion. Physical and chemical cleaning of the steel shall be accomplished by washing with an alkaline cleaner, followed by a spray treatment with a complex metallic phosphate solution to provide a uniform fine grained crystalline phosphate surface that shall provide both an excellent bond for the finish and enhance the protection provided by the finish against humidity and corrosive chemicals. 
After the phosphate treatment, the steel shall be dried and all steel surfaces shall be coated with a chemical and corrosion-resistant, environmentally friendly, electro statically applied powder coat finish. All components shall be individually painted, insuring that no area be vulnerable to corrosion due to lack of paint coverage. The coating shall then be cured by baking at elevated temperatures to provide maximum properties of corrosion and wear resistance. 

The completed finish system in standard colors shall meet the performance test requirements specified under PERFORMANCE TEST RESULTS.

- Performance Test Results (Chemical Spot Tests):

- Testing Procedure:
Chemical spot tests for non-volatile chemicals shall be made by applying 5 drops of each reagent to the surface to be tested and covering with a 1-1/4" dia. watch glass, convex side down to confine the reagent. Spot tests of volatile chemicals shall be tested by placing a cotton ball saturated with reagent on the surface to be tested and covering with an inverted 2-ounce wide mouth bottle to retard evaporation. All spot tests shall be conducted in such a manner that the test surface is kept wet throughout the entire test period, and at a temperature of 77° ±3° F. For both methods, leave the reagents on the panel for a period of one hour. At the end of the test period, the reagents shall be flushed from the surface with water, and the surface scrubbed with a soft bristle brush under running water, rinsed and dried. Volatile solvent test areas shall be cleaned with a cotton swab soaked in the solvent used on the test area. Immediately prior to evaluation, 16 to 24 hours after the reagents are removed, the test surface shall be scrubbed with a damp paper towel and dried with paper towels.

- Test Evaluation:
Evaluation shall be based on the following rating system.

- Level 0	–	No detectable change.

- Level 1	–	Slight change in color or gloss.

- Level 2	–	Slight surface etching or severe staining.

- Level 3	–	Pitting, cratering, swelling, or erosion of coating. Obvious and significant deterioration.

- After testing, panel shall show no more than three (3) Level 3 conditions.

- Test Reagents

- Test No.	Chemical Reagent	Test Method

- 1.	Acetate, Amyl	Cotton ball & bottle

- 2.	Acetate, Ethyl	Cotton ball & bottle

- 3.	Acetic Acid, 98%	Watch glass

- 4.	Acetone	Cotton ball & bottle

- 5.	Acid Dichromate, 5%	Watch glass

- 6.	Alcohol, Butyl	Cotton ball & bottle

- 7.	Alcohol, Ethyl	Cotton ball & bottle

- 8.	Alcohol, Methyl	Cotton ball & bottle

- 9.	Ammonium Hydroxide, 28%	Watch glass

- 10.	Benzene	Cotton ball & bottle

- 11.	Carbon Tetrachloride	Cotton ball & bottle

- 12.	Chloroform	Cotton ball & bottle

- 13.	Chromic Acid, 60%	Watch glass

- 14.	Cresol	Cotton ball & bottle

- 15.	Dichlor Acetic Acid	Cotton ball & bottle

- 16.	Dimethylformanide	Cotton ball & bottle

- 17.	Dioxane	Cotton ball & bottle

- 18.	Ethyl Ether	Cotton ball & bottle

- 19.	Formaldehyde, 37%	Cotton ball & bottle

- 20.	Formic Acid, 90%	Watch glass

- 21.	Furfural	Cotton ball & bottle

- 22.	Gasoline	Cotton ball & bottle

- 23.	Hydrochloric Acid, 37%	Watch glass

- 24.	Hydrofluoric Acid, 48%	Watch glass

- 25.	Hydrogen Peroxide, 3%	Watch glass

- 26.	Iodine, Tincture of	Watch glass

- 27.	Methyl Ethyl Ketone	Cotton ball & bottle

- 28.	Methylene Cloride	Cotton ball & bottle

- 29.	Mono Chlorobenzene	Cotton ball & bottle

- 30.	Naphthalene	Cotton ball & bottle

- 31.	Nitric Acid, 20%	Watch glass

- 32.	Nitric Acid, 30%	Watch glass

- 33.	Nitric Acid, 70%	Watch glass

- 34.	Phenol, 90%	Cotton ball & bottle

- 35.	Phosphoric Acid, 85%	Watch glass

- 36.	Silver Nitrate, Saturated	Watch glass

- 37.	Sodium Hydroxide, 10%	Watch glass

- 38.	Sodium Hydroxide, 20%	Watch glass

- 39.	Sodium Hydroxide, 40%	Watch glass

- 40.	Sodium Hydroxide, Flake	Watch glass

- 41.	Sodium Sulfide, Saturated	Watch glass

- 42.	Sulfuric Acid, 33%	Watch glass

- 43.	Sulfuric Acid, 77%	Watch glass

- 44.	Sulfuric Acid, 96%	Watch glass

- 45.	Sulfuric Acid, 77% and

- Nitric Acid, 70%, equal parts	Watch glass

- 46.	Toluene	Cotton ball & bottle

- 47.	Trichloroethylene	Cotton ball & bottle

- 48.	Xylene	Cotton ball & bottle

- 49.	Zinc Chloride, Saturated	Watch glass

- * Where concentrations are indicated, percentages are by weight.

- Performance Test Results (Heat Resistance):
Hot water (190° F - 205° F) shall be allowed to trickle (with a steady stream at a rate not less than 6 ounces per minute) on the finished surface, which shall be set at an angle of 45° from horizontal, for a period of five minutes. After cooling and wiping dry, the finish shall show no visible effect from the hot water treatment.

- Performance Test Results (Impact Resistance):
A one-pound ball (approximately 2" diameter) shall be dropped from a distance of 12 inches onto the finished surface of steel panel supported underneath by a solid surface. There shall be no evidence of cracks or checks in the finish due to impact upon close eye-ball examination.

- Performance Test Results (Bending Test):
An 18 gauge steel strip, finished as specified, when bent 180o over a 1/2" diameter mandrel, shall show no peeling or flaking off of the finish.

- Performance Test Results (Adhesion):
Ninety or more squares of the test sample shall remain coated after the scratch adhesion test. Two sets of eleven parallel lines 1/16" apart shall be cut with a razor blade to intersect at right angle thus forming a grid of 100 squares. The cuts shall be made just deep enough to go through the coating, but not into the substrate. They shall then be brushed lightly with a soft brush. Examine under 100 foot-candles of illumination. Note: This test is based on ASTM D2197-68, "Standard Method of Test for Adhesion of Organic Coatings".

- Performance Test Results (Hardness):

- The test sample shall have a hardness of 4-H using the pencil hardness test. Pencils, regardless of their brand are valued in this way: 8-H is the hardest, and next in order of diminishing hardness are 7-H, 6-H, 5-H, 4-H, 3-H, 2-H, F, HB, B (soft), 2-B, 3-B, 4-B, 5-B (which is the softest).

- The pencils shall be sharpened on emery paper to a wide sharp edge. Pencils of increasing hardness shall be pushed across the paint film in a chisel-like manner until one is found that will cut or scratch the film. The pencil used before that one-that is, the hardest pencil that will not rupture the film-is then used to express or designate the hardness.

- Table Tops:

- The tabletops shall be of 18/19mm Jet black Granite of a even surface and the level

- Tolerance less than 1 mm. The front edge of the granite shall be chamfered at an angle of 28 deg and smoothened. The back splash for the wall bench shall be granite 18/19mm thick material for an height of 4” from the finished table top level.

- Polypropylene Molded Sinks:

- The sinks should be injection molded from Poly propylene co-polymer resin. Polypropylene to have very high resistance to attack from a wide range of chemicals and the ability to withstand temperatures up to 100 deg C. The impact resistance should be high which will minimize damage during and after installation. The sinks should be with self draining base and should be suitable for mounting on top or underside of the work benches. The sinks should be compatible to a vast number of acids, alkalis and reagents. The size of the sink is 560Lx355Dx245Hmm and Bowl size is 500Lx293Dx245Hmm. This sinks shall have bottle trap with reducing coupler of size 51x31mm and with 38mm polypropylene pipe of one foot length.

- LABORATORY SERVICE FIXTURES AND SAFETY EQUIPMENTS

I. General

A.	All laboratory service fixtures shall have the construction and shall meet the performance requirements set forth in this specification. Fixture types shall be as indicated in the fixture schedule or fixture details included in either the project drawings or these specifications.

B.	All laboratory service fixtures and safety equipment shall be the product of one service fixture manufacturer to assure uniform appearance and ease of maintenance of the laboratory facility. Remote control valves and fittings furnished with fume hoods shall be the product of the same fixture manufacturer.

C.	All service fixtures shall be factory assembled (including the assembly of valves and shanks to turrets, flanges and other mounting accessories), and each fixture shall be individually factory tested. Fixtures shall be tested in the manner and at the pressures set forth below.

D.	Except as otherwise indicated, faucet and valve handles shall be forged brass Nylon type and shall have a color coded screw-on index disc. Color code requirements for indexing service fixtures shall follow DIN Standard 12920:1995.

II.	Finish

A.	General

1.	Laboratory service fixtures and safety equipment shall be furnished with a powder coated finish to enhance the appearance of the fitting and to protect against corrosion. Coating material shall be a blend of epoxy and polyurethane. The hybrid blend shall ensure a finish coating with and optimum combination of chemical resistance, mar and abrasion resistance and resistance to fading under ultraviolet (UV) light.

2.	Fittings inside fume hoods shall have an epoxy finish color-coded to match the fixture service index color. Coating material shall be free flowing epoxy powder with a particle size of 35-70 microns. Surfaces to be coated shall be (a) polished or sandblasted to produce a uniform fine-grained surface and (b) immersed in a phosphoric acid cleaning solution to remove thoroughly all oil, grease and other foreign substances. Following cleaning, coating material shall be electro statically applied to all exposed surfaces. After application, coating shall be fully baked to permit curing. Surfaces shall have a minimum coating thickness of 2 mils.

2.	Mar and Abrasion Resistance

Finishes shall have a pencil hardness of 2H-4H with adhesion substantial enough to withstand both direct and reverse impacts of 160 inch pounds. Finish shall have excellent mar resistance and be capable of withstanding scuffing, marring and other ordinary wear.

3.	Reparability

Finish shall be capable of surface repair in the event that a fixture is scratched or a surface rupture occurs. The service fixture manufacturer shall have available an air-drying aerosol coating, specially formulated to match the existing epoxy coating color, which may be applied in the field to repair coated surfaces.

III.	Water Faucets and Valves

A.	All faucets and valves for water service shall have a renewable unit containing all working components subject to wear, including a stainless steel replaceable seat and an integral adjustable volume control (designated by the suffix “AC”). The renewable unit shall be interchangeable among all faucets and valves for water service. The renewable unit shall be broached for position locking in the valve body. The unit shall have a high durometer thermoplastic valve disc and a molded TFE stem packing. The unit shall be capable of being readily converted from compression to self-closing, and vice versa, without disturbing the faucet body.

B.	Goosenecks shall have a separate outlet coupling with a 3/8" IPS female thread securely brazed to the gooseneck for attachment of serrated hose ends, aspirators and other outlet fittings. Rigid goosenecks shall have a 3/8" IPS male inlet thread and be threaded directly into the faucet body so as to be absolutely rigid. Swing goosenecks shall utilize a TFE packing with an externally adjustable packing nut.

C.	Vacuum breakers, where required and indicated by the fixture number, shall be integral with the gooseneck. Vacuum breakers shall have a forged brass body, a renewable seat and an ultra light float cup with a silicone gasket for fine flow control. Vacuum breakers shall not spill over at low water volume. Vacuum breakers shall be certified by the American Society of Sanitary Engineers (ASSE) under Standard 1001.

D.	All fixtures for water service shall meet the requirements of ANSI/ASME A112.18.1M-1989 and be certified by the Canadian Standards Association (CSA) under Standard CAN/CSA B.125.M89.

E. Water faucets and valves shall be fully assembled and individually tested at 80 pounds per square inch (PSI) water pressure.

IV. Safety Equipment

All emergency eye wash and shower equipment should comply with ANSI Z358.1-1990.

SPECIFICATION OF SAFETY CABINET

Solvent Storage:

- Safety Cabinet are produced in accordance with NFPA 30 Chapter 9.5.3 and OSHA 29  CFR 1910.106 regulations

- Safety Cabinets of 12 gallons and greater are FM Global tested and approved

- 2” deep liquid tight containment sump covering the entire floor of the cabinet

- 18-gauge double walled steel construction, along with 1-1/2” air spaces between the walls, store flammable liquids and waste securely and safely

- Fully welded construction, increasing fire protection by reducing gapping

- Integrally welded, interlocking shelf hangers increase stability while reducing hardware

- Durable powder coat paint will resist solvents, acids and alkalis

- Two grounding attachment points at the rear of all cabinets for easy grounding

- Continuous full door height piano hinges

- FM & UL approved fusible-link hold open feature ensures the door closes should the temperature outside the cabinet exceed 165 degrees Fahrenheit

- Self-closing, self-latching synchronized doors ensure that the left door closes prior to the right door

- Polyethylene trays for galvanized steel shelves offer additional protection and have a slightly raised curved edge to contain the spills

- Polyethylene trays in the bottom sill area catch incidental spills and leaks

- Upper and lower diametrically opposed side vent with flame arrestor of proper venting when specified.

- Laboratory grade formulation meets SEFA 8 chemical requirement

Acid Storage:

- All models have the same quality features as flammable cabinets including: double-wall construction, dual vents, grounding wire connection, adjustable shelves, leak proof sills, three-point self-latching doors and leveling feet.

- To resist aggressive chemicals, acid cabinets also include polyethylene trays attached to galvanized steel shelves and a separate polyethylene liner for the bottom sump.

- The liner can be removed for easy cleaning of drips and leaks.

- The popular 30-gallon two door cabinet also includes an extra polyethylene top work tray which can be secured to cabinet-top for a handy work surface.

- An all-epoxy, baked-on powder coat finish, inside-and-out, provides increased chemical resistance.

- Paint is exclusively formulated to resist the acids, bases and solvents often used in laboratories.

- APPLICABLE CODES & STANDARDS

  - SEFA 3 – Scientific Equipment and Furniture Association

  - SEFA 8 - Scientific Equipment and Furniture Association

  - NFPA 30  - National Fire Protection Association

  - NFPA-45 - National Fire Protection Association

  - UL - Underwriters Laboratories

  - ASTM D552 – Bending Test

- CHAPTER-02

- FUMEHOOD SPECIFICATIONS

DESCRIPTION OF WORK

- SUMMARY AND SCOPE

- Section Includes:
Furnish and install all fume hoods, work tops, and understructures as shown on drawings.

- Accessorization:

Furnishing and delivering all service outlets, accessory fittings, electrical receptacles and switches as listed in these specifications, equipment schedules or as shown on drawings.  Fittings attached to the fume hood superstructure shall be mounted at the factory.

- Removal of all debris, dirt and rubbish accumulated as a result of the installation of the fume hoods to an on-site container provided by others, leaving the premises clean and orderly.

- STANDARD FUME HOOD PERFORMANCE REQUIREMENTS

- Fume hoods shall be of complete airfoil design to insure maximum operating efficiency.  Foil sections at the front facias of the hood shall minimize eddying of air currents at the hood face and the rear baffle system shall minimize turbulence in the upper portion of the hood interior.

- Standard Fume Hood Type Variable Air Volume: 
The fume hoods shall be of the variable air volume type in which the exhaust air volume varies proportionally to the hood opening when used with a hood face velocity controller system. The air bypass shall be RESTRICTED AS PER THE VAV Manufacturer’s recommendation.

2.01	MATERIALS AND CONSTRUCTION

- Fume Hood Superstructure Frame: 
A free-standing rigid frame structure of steel angle shall be provided to support exterior panels and interior liner and baffle panels.  To allow for maintenance and replacements, the interior liner panels shall be removable without disassembly of the frame structure and outer steel panels.  Likewise, the exterior steel panels shall be removable without disassembly of the frame structure and inner liner panels.  Fume hoods that require disassembly of the superstructure for liner replacement are not acceptable.

- Fume Hood Interior Walls: 
Double wall ends, not more than 4” wide, shall be provided to maximize interior working area.  The area between the double wall ends shall be closed to house the remote control valves.  The front vertical facia section shall have a full 135 degree 1” radius at the front leading edge to provide a streamlined section and insure smooth even flow of air into the hood.  The vertical facias shall contain the required service controls, electrical switches and receptacles.  The hood interior end panels and sash track shall be flush with the facia to prevent eddy currents and back flow of air.

- Fume Hood Airfoil: 
A streamlined airfoil shall be integral at the bottom of the hood opening on bench and distillation hoods.  This foil shall provide a nominal 1” open space between the foil and the top front edge of the work surface to direct an air stream across the work surface to prevent back flow of air.  The airfoil shall extend back under the sash, so that the sash does not close the 1” opening.  The foil shall be removable to allow large equipment into the hood.  The foil shall be of 12-gauge steel to resist denting and flexing.  Walk-in hoods shall have a stop located at the bottom of the sash track that will ensure a nominal 1” opening between the bottom of the sash and the floor.

- Fume Hood Top Panel:

Restricted Bypass Configuration:
The top front panel shall be of the same material as the exterior facia.

- Fume Hood Baffles :

A stable, non-adjustable baffle with three fixed horizontal slots shall be provided to aid in distributing the flow of air into and through the hood.  The baffle shall be spaced out 2-1/4” from the back liner.  The baffle shall be removable for cleaning

- Fume Hood Duct Collar :

A 12” diameter polyethylene bell-mouthed duct collar shall be located in the top of the hood plenum chamber.  Coated common steel duct collars are not acceptable. Lab vendor has to Supply ONLY Manual Damper with Flexible Hose, Tie-in connection to the Main Exhaust system will be done by Other Vendors

- Fume Hood Lighting: 
A one-tube, energy-efficient, T-5 fluorescent light fixture of the size given below shall be provided in the hood roof. Illumination at 13” above the worksurface shall be at least 100 foot-candles.

Hood Size, Ft.					Nominal Fixture Length, Ft. 
         5							4

The light fixtures shall be isolated from the hood interior by a 1/4” thick tempered glass panel sealed from the hood cavity.

- Fume Hood Sash:

Combination Sash: 
A combination sash shall be provided.  The sash shall have horizontal sliding glass panels in a vertical rising steel frame.  The bottom of the sash frame shall have a full length metal handle.  The sash track shall be a neutral colored polyvinyl chloride set flush with the interior liner panels to minimize turbulence.  The sash shall be counterbalanced with a single weight to prevent tilting and binding during operation.  The glass panels shall be 1/4” laminated safety float glass mounted on metal rollers in an aluminum track.

- Fume Hood Plumbing Service:

Utility services like Nitrogen, Vacuum, Compressed Air and Raw water shall consist of remote control valves as selected located within the end panels, controlled by extension rods projecting through the control panels of the hood, with color coded plastic handles.  Interior fitting for gases and water shall be nylon panel flanges and angle serrated hose connectors, color coded.  Interior fittings for distilled water shall consist of a bronze tin lined, white color-coded, panel flange and angle serrated hose connector.  Interior fittings for steam shall consist of a cast bronze flange and angle serrated hose connector with a chemical resistant metallic bronze finish.  Water goosenecks shall be cast bronze with a chemical resistant metallic bronze finish.  All plumbing fittings shall be factory installed and piped between the valve and the outlet.  Inlet piping shall have a single-point connection for each valve provided and carried to a point 1” above the fume hood roof.  Points of final service connection by other trades shall be at the stub provided by the fume hood manufacturer.

- Fume Hood Electrical Service:

The hood superstructure shall be pre-wired and contain wire gauge, connections, fixtures and wire color coding.  Wiring electrical services shall consist of two duplex receptacles and a light switch.  4 nos of 5/15 Amps (Make: North West), 230 Volt AC, and 3-wire polarized grounded with ground fault interruption.  The receptacles shall be of specification grade, side wired only, to insure a positive connection.  The light switch shall be 5 Amps. 230 volt AC and 3-wire polarized grounded.  Wiring shall terminate in one 6” x 6” x 4” service junction box located on the fume hood roof

- Hood Work Surface:

Black Granite:

Hood worksurface shall be 1-1/4” thick jet black granite made in the form of a watertight pan, not less than 3/8” deep to contain spillage with a 8”& 6” wide safety ledge across the front edge.  A cup drain flush with the recessed worksurface shall be provided.  The worksurface and cup drain shall be available in black.

- Polyethylene Cup Sinks:

Molded polyethylene cup drains shall be molded in one-piece of acid-resistant polyethylene. They shall have an integral mounting flange and an integral tailpiece with a 1-1/2" I.P.S. male straight thread outlet.

- Access Opening:
The interior end liner panels shall be furnished with an opening that provides access to the service piping and valves to facilitate installation and maintenance.  The openings shall be covered with a removable panel with rounded corners.  Panels that require tools to remove are not acceptable.  The panel shall provide an overlapping seal on all edges.

- Fume Hood Finish:
After the component parts have been completely welded together and before finishing, they shall be given a pre-paint treatment to provide excellent adhesion of the finish system to the steel and to aid in the prevention of corrosion.  Physical and chemical cleaning of the steel shall be accomplished by washing with an alkaline cleaner, followed by a spray treatment with a complex metallic phosphate solution to provide a uniform fine grained crystalline phosphate surface that shall provide both an excellent bond for the finish and enhance the protection provided by the finish against humidity and corrosive chemicals. 

After the phosphate treatment, the steel shall be dried and all steel surfaces shall be coated with a chemical and corrosion-resistant, environmentally friendly, electrostatically applied powder coat finish. All components shall be individually painted, insuring that no area be vulnerable to corrosion due to lack of paint coverage. The coating shall then be cured by baking at elevated temperatures to provide maximum properties of corrosion and wear resistance.  

The completed finish system in standard colors shall meet the performance test requirements specified under PERFORMANCE TEST RESULTS.

- Performance Test Results (Chemical Spot Tests):

- Testing Procedure:
Chemical spot tests for non-volatile chemicals shall be made by applying 5 drops of each reagent to the surface to be tested and covering with a 1-1/4" dia. watch glass, convex side down to confine the reagent. Spot tests of volatile chemicals shall be tested by placing a cotton ball saturated with reagent on the surface to be tested and covering with an inverted 2-ounce wide mouth bottle to retard evaporation.  All spot tests shall be conducted in such a manner that the test surface is kept wet throughout the entire test period, and at a temperature of 77° ±3° F. For both methods, leave the reagents on the panel for a period of one hour. At the end of the test period, the reagents shall be flushed from the surface with water, and the surface scrubbed with a soft bristle brush under running water, rinsed and dried. Volatile solvent test areas shall be cleaned with a cotton swab soaked in the solvent used on the test area. Immediately prior to evaluation, 16 to 24 hours after the reagents are removed, the test surface shall be scrubbed with a damp paper towel and dried with paper towels.

- Test Evaluation:
Evaluation shall be based on the following rating system.

- Level 0	–	No detectable change.

- Level 1	–	Slight change in color or gloss.

- Level 2	–	Slight surface etching or severe staining.

- Level 3	–	Pitting, cratering, swelling, or erosion of coating. Obvious and significant deterioration.

- After testing, panel shall show no more than three (3) Level 3 conditions.

- Test Reagents

- Test No.	Chemical Reagent	Test Method

- 1.	Acetate, Amyl	Cotton ball & bottle

- 2.	Acetate, Ethyl	Cotton ball & bottle

- 3.	Acetic Acid, 98%	Watch glass

- 4.	Acetone	Cotton ball & bottle

- 5.	Acid Dichromate, 5%	Watch glass

- 6.	Alcohol, Butyl	Cotton ball & bottle

- 7.	Alcohol, Ethyl	Cotton ball & bottle

- 8.	Alcohol, Methyl	Cotton ball & bottle

- 9.	Ammonium Hydroxide, 28%	Watch glass

- 10.	Benzene	Cotton ball & bottle

- 11.	Carbon Tetrachloride	Cotton ball & bottle

- 12.	Chloroform	Cotton ball & bottle

- 13.	Chromic Acid, 60%	Watch glass

- 14.	Cresol	Cotton ball & bottle

- 15.	Dichlor Acetic Acid	Cotton ball & bottle

- 16.	Dimethylformanide	Cotton ball & bottle

- 17.	Dioxane	Cotton ball & bottle

- 18.	Ethyl Ether	Cotton ball & bottle

- 19.	Formaldehyde, 37%	Cotton ball & bottle

- 20.	Formic Acid, 90%	Watch glass

- 21.	Furfural	Cotton ball & bottle

- 22.	Gasoline	Cotton ball & bottle

- 23.	Hydrochloric Acid, 37%	Watch glass

- 24.	Hydrofluoric Acid, 48%	Watch glass

- 25.	Hydrogen Peroxide, 3%	Watch glass

- 26.	Iodine, Tincture of	Watch glass

- 27.	Methyl Ethyl Ketone	Cotton ball & bottle

- 28.	Methylene Cloride	Cotton ball & bottle

- 29.	Mono Chlorobenzene	Cotton ball & bottle

- 30.	Naphthalene	Cotton ball & bottle

- 31.	Nitric Acid, 20%	Watch glass

- 32.	Nitric Acid, 30%	Watch glass

- 33.	Nitric Acid, 70%	Watch glass

- 34.	Phenol, 90%	Cotton ball & bottle

- 35.	Phosphoric Acid, 85%	Watch glass

- 36.	Silver Nitrate, Saturated	Watch glass

- 37.	Sodium Hydroxide, 10%	Watch glass

- 38.	Sodium Hydroxide, 20%	Watch glass

- 39.	Sodium Hydroxide, 40%	Watch glass

- 40.	Sodium Hydroxide, Flake	Watch glass

- 41.	Sodium Sulfide, Saturated	Watch glass

- 42.	Sulfuric Acid, 33%	Watch glass

- 43.	Sulfuric Acid, 77%	Watch glass

- 44.	Sulfuric Acid, 96%	Watch glass

- 45.	Sulfuric Acid, 77% and

- Nitric Acid, 70%, equal parts	Watch glass

- 46.	Toluene	Cotton ball & bottle

- 47.	Trichloroethylene	Cotton ball & bottle

- 48.	Xylene	Cotton ball & bottle

- 49.	Zinc Chloride, Saturated	Watch glass

- * Where concentrations are indicated, percentages are by weight.

- Performance Test Results (Heat Resistance):
Hot water (190° F - 205° F) shall be allowed to trickle (with a steady stream at a rate not less than 6 ounces per minute) on the finished surface, which shall be set at an angle of 45° from horizontal, for a period of five minutes. After cooling and wiping dry, the finish shall show no visible effect from the hot water treatment.

- Performance Test Results (Impact Resistance):
A one-pound ball (approximately 2" diameter) shall be dropped from a distance of 12 inches onto the finished surface of steel panel supported underneath by a solid surface. There shall be no evidence of cracks or checks in the finish due to impact upon close eye-ball examination.

- Performance Test Results (Bending Test):
An 18 gauge steel strip, finished as specified, when bent 180o over a 1/2" diameter mandrel, shall show no peeling or flaking off of the finish.

- Performance Test Results (Adhesion):
Ninety or more squares of the test sample shall remain coated after the scratch adhesion test. Two sets of eleven parallel lines 1/16" apart shall be cut with a razor blade to intersect at right angle thus forming a grid of 100 squares.  The cuts shall be made just deep enough to go through the coating, but not into the substrate.  They shall then be brushed lightly with a soft brush.  Examine less than 100 foot-candles of illumination.  Note:  This test is based on ASTM D2197-68, "Standard Method of Test for Adhesion of Organic Coatings".

- Performance Test Results (Hardness):

- The test sample shall have a hardness of 4-H using the pencil hardness test.  Pencils, regardless of their brand are valued in this way:  8-H is the hardest, and next in order of diminishing hardness are 7-H, 6-H, 5-H, 4-H, 3-H, 2-H, F, HB, B (soft), 2-B, 3-B, 4-B, 5-B (which is the softest).

The pencils shall be sharpened on emery paper to a wide sharp edge.  Pencils of increasing hardness shall be pushed across the paint film in a chisel-like manner until one is found that will cut or scratch the film.  The pencil used before that one-that is, the hardest pencil that will not rupture the film-is then used to express or designate the hardness.

- Fume Hood Dimensions
Double wall end panel thickness shall not exceed 4”.  Interior clear working height shall be not less than 41-3/4” at any location in the interior of the hood on bench hoods. Interior depth from the back of the sash to the front of the rear baffle shall not be less than 25-1/4”.  The sash opening shall be not less than 28” in height above the worksurface on bench hoods.

- Fume Hood Liners :

Interior liner panels shall be 1/4” thick fiberglass reinforced polyester sheet.  Interior liner panels shall be fastened using stainless steel screws with plastic covered heads.

- Liner Tests – Chemical Spot Tests – 24 Hours

- Chemical spot test shall be made by applying 10 drops (approximately 1/2 cc) of each reagent to the surface to be tested.  Each reagent (except those marked **) shall be covered with a 1-1/2” diameter watch glass, convex side down to confine the reagent.  Spot tests of volatile solvents marked ** shall be tested as follows:  A 1” or larger ball of cotton shall be saturated with the solvent and placed on the surfaces to be tested.  The cotton ball shall then be covered by an inverted 2-ounce, wide mouth bottle to retard evaporation.  All spot tests shall be conducted in such a manner that the test surface is kept wet throughout the entire 24-hour test period and at a temperature of 77 degrees F. + 3 degrees F.

- At the end of the test period, the reagents shall be flushed from the surfaces with water and the surface scrubbed with a soft bristle brush under running water, rinsed, and dried.  Volatile solvent test areas shall be cleaned with a cotton swab soaked in the solvent used on the test area.  Spots where dyes have dried shall be cleaned with a cotton swab soaked in alcohol to remove the surface dye.  The test panel shall then be evaluated immediately after drying.

RESULTS:                                                  1           2          3           4           5
 1.  Acetic Acid	98%		     	A	B	B	B	A
 2.  Acetone **			A	D	A	A	A
 3.  Acid Dichromate			A	A	A	A	A
 4.  Ammonium Hydroxide ** 28%	A	A	B 	B	A
 5.  Amyl Acetate **			A	A	A	A	A
 6.  Benzene **			A	A	A	A	A
 7.  Butyl Alcohol **			A	A	A	A	A
 8.  Carbon Tetrachloride **		A	A	A	A	A
 9.  Chloroform **			A	D	A	A	A
10.  Chromic Acid	      60%	B 	B 	C	C	A
11.  Cresol				A	A	A	A	A
12.  Dichloroacetic Acid		A	D	B	A	A
13.  Dimethylformamide		A	A	A	A	A
14.  Dioxane **			A	A	A	A	A
15.  Ethyl Acetate **			A	A	A	A	A
16.  Ethyl Ether **			A	A	A	A	A
17.  Ethyl Alcohol **			A	A	A	A	A
18.  Formaldehyde			A	A 	A	A	A
19.  Formic Acid 	       90%	A	A	A	A	A
20.  Furfural **			B	B	A	A	C
21.  Gasoline **			A	A	A	A	A
22.  Hydrochloric Acid	  37%		A	A	B	B	A
23.  Hydrofluoric Acid     48%		B	D	D	D	A
24.  Hydrogen Peroxide  30%		A	A	A	A	A
25.  Methyl Ethyl Ketone **		A 	A	A	A	A
26.  Methyl Alcohol **		A	A	A 	A	A
27.  Methylene Chloride **		A	D	A	A	A
28.  Monochlorobenzene **		A	A	A	A	A
29.  Naphthalene **			A	A	A	A 	A
30.  Nitric Acid	20%			B	A	B	A	A
31.  Nitric Acid  30%			B	A	B	A	A
32.  Nitric Acid  70%			B	D	B	A	A
33.  Phenol **   85%			A	C	A	A	A
34.  Phosphoric Acid 85%		A	A	B	A	A
35.  Silver Nitrate			B	C	A	A	C
36.  Sodium Hydroxide 40%		A	D	A	A	A
37.  Sodium Hydroxide 20%		A	D	A	A	A
38.  Sodium Hydroxide    10%		A	D	A	A	A
39.  Sodium Hydroxide Flake		A	B	A	A	A
40.  Sodium Sulfide			A	B	A	A	A
41.  Sulfuric Acid   77%		A	A	C	A	A
42.  Sulfuric Acid   96%		C	D	C	A	C
43.  Sulfuric Acid   33%		A	A	C	A	A
44.  Tincture of Iodine			A	C	B	B	A
45.  Toluene **			A	A	A	A	A
46.  Trichlorethylene **		A	A	A	A	A
47.  Xylene **				A 	A	A	A	A
48.  Zinc Chloride			A	A	B	A	A
49.  Nitric 70%/Sulfuric Acid 77%*	B 	B	B	A	A

*	Equal parts of Nitric Acid 70% and Sulfuric Acid 77%.  
**	Indicates these solvents tested with cotton and jar method

- Fume Hood Base Cabinets

- Standard Steel

- Unless otherwise indicated base units under hoods shall be fabricated of cold rolled prime grade roller leveled furniture steel.  Gauges of steel used in construction shall be 18 gauge except as follows:

- Corner gussets for leveling bolts and apron corner braces, 12 gauge.

- Hinge reinforcements, 14 gauge.

- Top and intermediate front horizontal rails, apron rails and reinforcement gussets, 16 gauge.

- Drawer assemblies 20 gauge.

- Performance of the painted surfaces shall match that of the fume hood outer panels.

- MATERIAL OF CONSTRUCTION

- Fume Hood superstructure	: 18 gauge CRC Sheets, Electrode position                          Powder coated 80-100 micron

- Table top			:  32 mm Jet Black Granite Table top

- Electrical sockets		:  PVC

- Gas fixtures			: Brass Lacquer Coated

- Internal piping			:  SS304

- Vacuum Fixtures		: Brass Lacquer Coated

- Water fixtures			: Brass Lacquer Coated

- Electrical cables		: Copper wire with PVC Sheath

- 3.0 APPLICABLE CODES & STANDARDS:

ASHRAE Standard 110.1995 	- Method of Testing Performance of

Laboratory Fume Hoods

NSF STD#49 			- Photometric Method of Testing

NIH03-112C 			- National Institute of Health Specification

UL 					- Underwriters Laboratories

ASTM D552 			- Bending Test

NFPA-45 				- National Fire Protection Association

Note: VENDOR MUST HAVE ASHRAE TESTING FACILITY AT MANUFACTURING PLANT & ABLE TO CONDUCT THE SAME IN THE SITE.