|  | Hkkjrh; izkS¦ksfxdh laLFkku enzkl psUuS 600 036 INDIAN INSTITUTE OF TECHNOLOGY MADRAS Chennai 600 036 HkaMkj ,oa Ø; vuqHkkx STORES & PURCHASE SECTION Email: adstores@iitm.ac.in nwjHkk"k% ¼044½ 2257 8285@8286@8287@8288 QSDl% ¼044½ 2257 8292 Telephone : (044) 2257 8285/8286/8287/8288 FAX: (044) 2257 8292 |  |
| --- | --- | --- |

A.V. SUDARSANAM                        	            SPS/UPS-1 kVA Tech Enq./RC/2014/SPL

DEPUTY REGISTRAR (S&P)                                                                 Date. 27.11.2014

Due date	:15.12.2014

Time 	:	05.00 P.M.

Dear Sir/Madam,

Quotations are invited for procurement of UPS 1kVA UPS True On Line, Sine wave Output without isolation transformer and with 15 minutes battery back up under Rate Contract.  Dealers must submit an authorized dealership certificate from the manufacturer for 1 KVA UPS. Otherwise the quotations will be summarily rejected.

Kindly make arrangements to deliver one sample along with Batteries to the Head, Central Electronics Centre (CEC), IIT Madras, Chennai 600036 for necessary Testing and Technical evaluation on or before 15.12.2014 @ 5 pm.    For any technical clarification, please contact, CEC, and the contact No.044 2257 4947.

To consider your products under Rate Contract, kindly furnish the technical particulars along with Product Catalogue/s, Test Certificates and list of clients for the following UPS configurations in the prescribed formats (available in our web site www.tender.iitm.ac.in) to the Head, Central Electronics Centre, IIT Madras, with a copy to the undersigned on or before 15.12.2014 @ 5pm

The UPS and Batteries must function as per the specifications at room temperature without Air-Conditioners.

You may please note that, short-listing of suppliers for particular model/s for receiving of the commercial quote will be made only after testing and technical evaluation of the model/s.

Yours faithfully,

Deputy  Registrar (S & P)

Encl: As Above

TECHNICAL SPECIFICATIONS

1kVA UPS True On Line, Sine wave Output without isolation transformer

Technology  :

PWM technology in True on-line operation, employing double conversion method using

MOSFETs / IGBTs.

Method of Inversion  :

Adaptive pulse width modulation or weighted pulse width modulation with high

Frequency switching  (>10 kHz for MOSFETs and  >5kHz for IGBTs).

Test Parameters:

1.     Input Voltage Range @ F.L				              :  180V-270V AC

2.     Input Power Factor @ F.L					:  > 0.95

3.     Input Frequency Variation					: 50 Hz ± 5%

4.     Total Energy storage capacity of Battery ( in one               :

String)  @ F.L and @ Non-A/C environment

| Backup time | Watt Hr. required |
| --- | --- |
|  | 36V Bus | 48V Bus |
| 15 min | >250 Watt Hr | >250 Watt Hr |

5.    AC Output Voltage and steady state Regulation @ F.L       	: 230V AC; better than  ± 1%

6.     Transient Voltage Regulation at Step Load 			: < 5%

7.     Maximum deliverable continuous Output Power 			: >800W

8.     Output Frequency 						: 50 Hz ± 4%(Synchronous  to mains)

50 Hz ( 0.5%(Free running ).

9.     Efficiency

(i)  Battery mode						: > 80%

(ii) Mains mode		   				: > 80%

10.     THD @ F.L  						              : <3% (for linear load); <5%(for nonlinear load)

11.   Crest Factor @ F.L						: > 3 : 1

12. Over Load Duration @ 110%, 125% and 150% of F.L	: 5 min, 1 min and  2 sec respectively

13.   Static bypass switch : Bi-directional with change over time less than 10 milliseconds in free running mode and

instantaneous in synchronous mode from Inverter to Bypass and vice-versa.

14.  Temperature and Humidity

(i)    Operating Temperature Range				: upto 40ºC

(ii)   Humidity						: upto 95% Rh

15.   Noise level (at 1 meter)				  	: < 45 dB

16.   Conformance to Standards

(i)   EMC Standards					  	: IEC 801-2,3,4,5

(ii)  Emission Standard					: EN55022 Class B

(iii) Safety Standard					  	: EN 50091-1

Battery Charger Operation:

Float-cum-boost charger with automatic boost/trickle charger modes with current limiting            features.  It’s characteristics shall be such as to match the float/ boost charging of the batteries as per battery characteristic, for battery life enhancement. High frequency chargers preferred.

Protection Features:

a) Current limiting ,Over load and Short circuit protection.

b) Phase locking mechanism with mains frequency.

c) Over voltage / Under voltage protection.

d) All other protection systems as required for safety  of the system.

Warranty and AMC

1.  3 years Warranty Period for UPS  as well as  Batteries.

2. Comprehensive AMC covering the batteries, after the expiry of warranty period

Important instructions:

a)  Quote should indicate the Model/Series Name and Model Number of UPS